## Slide 1
HVAC Schematic Symbols
Contact – normally closed
Contact – normally open
Pressure Switch – normally open
Temperature Switch – normally closed
Thermal Overload – normally closed
Transformer
ANSWER SHEET

## Slide 2
Little to no Superheat Refrigerant flood back
Compressor cold or frozen
Split-System Air Conditioner
ANSWER SHEET
Basic troubleshooting
Name three (3) things that can cause high head pressure.
Dirty Condenser coil Bad Condenser fan
Overcharged Air in the system
Name three (3) things that can cause low suction pressure.
Dirty Evaporator coil Bad evaporator fan
Loss of charge Blocked or closed metering device
Dirty air filter
What may indicate that a TXV is stuck closed?
High superheat Low section pressure
Compressor hot to the touch
What may indicate that a TXV is stuck open?
Ohm out the coil
Check the continuity of the dry contacts while energized/de-energized
How can you check to see if a fan relay, or contactor, is bad?
Low voltage Bad capacitor
Worn bearings
What may cause high amp draw on a blower, or condenser motor?
Bad contactor Off on thermal overload
Off on pressure control safety
List some possibilities that keep a compressor from operating when you have a proven call for cooling?
None, or zero ohms
What resistance would you expect to see across a set of closed contacts?
24 volts
What voltage would you expect to see between common and terminal “G” with the equipment energized, and the fan in the “on” position?